Town of Beech Mountain

Wastewater Collection and Treatment

System Performance Report

2024-2025 Fiscal Year

This report provides information on the collection and treatment system operated by the Town of Beech Mountain Public Utilities Department. Summarized herein is general information and performance data covering the period from July 1, 2023, to June 30th, 2024.  A copy of this report is available to the public upon request. Please direct questions about this report to the Public Works and Utilities office at (828) 387-9282.

Collection and Treatment System Description

The Town of Beech Mountain Wastewater collection and treatment system consists of approximately 60 miles of sewer pipe, five lift/pump stations, and two treatment plants.  The Town collection system is operated under Permit # WQCS00210.

The Town is permitted to treat wastewater at two facilities:  Pond Creek Wastewater Treatment Plant (PCWWTP) and Grassy Gap Creek Wastewater Treatment Plant (GGCWWTP). The Pond Creek WWTP operates under National Pollutant Discharge Elimination System (NPDES) Permit # NC0069761.  Wastewater is collected via a gravity system with two pump stations to a 0.400 million gallons per day extended aeration treatment plant with UV disinfection.  No tonnage of biosolids for FY 2023-2024 have been disposed of. The Town maintains a Biosolids Disposal DCAR Residuals Management Systems Land Application Permit WQ0002523.

The Grassy Gap Creek WWTP operates under NPDES Permit # NC002273. Wastewater is collected via a gravity system with two pump stations to a 0.080 million gallons per day extended aeration treatment plant with C12 disinfection.  Combined, the facilities have a treatment capacity of 0.480 million gallons/day.  Reference Table 1 and Table 2 for Discharge Monitoring Report Statistics.

Performance Summary

Between July 1st, 2024, and June 30th, 2025,

Wastewater Treatment facilities had the following Violations in the fiscal year.

| Pond Creek WWTP NC0069761 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sample Location | Parameter | Date | Limit/Reported Value |  | Type of Violation |
| 001 Effluent | Nitrogen, Ammonia Total | 7/6/2024 | 6 / 6.19 |  | Weekly Average Exceeded |
| 001 Effluent | Nitrogen, Ammonia Total | 7/31/2024 | 2 | 2 / 5.02 | Monthly Average Exceeded |

| Grassy Gap WWTP NC0022730 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sample Location | Parameter | Date | Limit/Reported Value |  | Type of Violation |
| 002 Effluent | Coliform, Fecal MF, MFC Broth, 44.5 C (31616) | 7/31/2024 | 200 / 232.28 |  | Monthly Geometric Mean Exceeded |

Hurricane Helene caused severe damage to the Beech Mountain Collection system due to many pipes and inlets being along various streams and roadway intersections.  Repairs were quickly made, and all systems were returned to standard operations within 12 days.  Each site was individually classified and reported to the State of North Carolina because of the September 27th, 2024, event.  “Severe natural conditions: Hurricane Helene” were the root cause.

- 364 Locust Ridge Rd. – Pond Creek WWTP REPAIRED 9/30/2024 estimated 25,000 gallons

- 1318 Pine Ridge Rd. – Grassy Gap WWTP REPAIRED 9/30/2024 estimated 25,000 gallons

- 1482 Pine Ridge Rd. – Buckeye Lift Station REPAIRED 9/30/2024 estimated 10,000 gallons

- 107 Pond Creek T0336 – lid knocked off during road failure and manhole filled with debris blocking outlet   -REPAIRED 10/7/2024 estimated 1,000 gallons

- 301 Jackpine Rd. T0222- lid knocked off during bank failure and manhole filled with debris blocking outlet -REPAIRED 10/7/2024 estimated 1,000 gallons

- 145 Hornbeam Rd. - Pipe section T0531 to J0577 – Pipe section broken by rocks/extreme flow from outside. REPAIRED 10/7/2024 estimated 1,000 gallons

- Outfall adjacent to 145 Hornbeam Rd. - Pipe Section J0577 to J0576- Pipe section broken by rocks/extreme flow from outside. REPAIRED 10/7/2024 estimated 1,000 gallons

- 314 Charter Hills Rd. - J0281    stream flow tore pipe from ground feeding manhole.  REPAIRED 10/7/2024 estimated 1,000 gallons

- 271 Greenbriar – Dislocated manhole during roadway failure and stream flow. REPAIRED 10/8/2024 estimated 4,000 gallons

- Outfall Adjacent to 106 Pond Creek Ln. - T0779 to T0781 100’ section of pipe disjointed by exterior stream flow.  REPAIRED  10/9/2024 estimated 2,000 gallons

- 364 Locust Ridge Rd Pipe section between T0440 and T0476 – Pipe section dislocated by stream volume at crossing between manholes. REPAIRED 10/9/2024 estimated 4,000 gallons

The 2022 Water and Sewer Rehabilitation Project is underway.  This project focuses on the replacement and rehab as well as many manhole repairs in 17,000 feet of sewer main in the continuing effort to reduce inflow and infiltration to our system.  Project completion is expected by November 2025.

The Utility continues to plan for future repairs in our system and ask for customer involvement in reducing SSO volume and the reduction of water getting into the system.  Help us to keep the system free of materials that cause blockages by not dumping debris, fats, oils, or grease into the system.

To report a sewer spill, please contact the Town of Beech Mountain Emergency Dispatch at 828-387-2342. For questions regarding the Town Utilities programs or additional information regarding this report, please contact Mr. Daniel Davis, Utilities Director at (828) 387-9282. Copies of this report may be obtained by calling Public Works at (828)387-3828 and requesting a copy or Town Hall at (828) 387-4236 and requesting a copy. This report is also available at the town website, TownofBeechMountain.com, https://townofbeechmountain.com/water-sewer/#water-reports.

This document includes details about monitoring system discharges and overflows from our system, the preventative maintenance program the Commission has established to prevent potential problems and the degree to which we complied with State and Federal standards during the fiscal year ending June 30, 2024.

Certification of Accuracy

I certify under penalty of law that this report is complete and accurate to the best of my knowledge.  I further certify that this report has been made available to all persons or customers of the Town of Beech Mountain Municipal water and sewer system and have been notified of the availability of this report.

_______Daniel E. Davis_______________________________	Date __8/8/2025________

Daniel Davis

Public Utilities Director

Town of Beech Mountain

Appendices:

Table 1: Pond Creek WWTP Effluent Flow Monthly Statistics. Total effluent flow discharged from treatment plant is measured in million gallons (MG).  Min, max and average daily values are represented in units of millions of gallons per day (MGD).

| Pond Creek WWTP | Total (MG) | Min (MGD) | Max (MGD) | Average (MGD) |
| --- | --- | --- | --- | --- |
| July ‘24 | 3.97 | 0.08 | 0.18 | 0.128 |
| August ‘24 | 3.47 | 0.04 | 0.15 | 0.112 |
| September ‘24 | 4.59 | 0.05 | 0.4 | 0.153 |
| October ‘24 | 3.04 | 0.05 | 0.34 | 0.098 |
| November ‘24 | 2.76 | 0.0001 | 0.21 | 0.092 |
| December ‘24 | 6.48 | 0.07 | 0.61 | 0.209 |
| January ‘25 | 4.71 | 0.09 | 0.405 | 0.152 |
| February ‘25 | 10.95 | 0.11 | 1.00 | 0.365 |
| March ‘25 | 5.27 | 0.09 | 0.29 | 0.170 |
| April ‘25 | 3.69 | 0.08 | 0.32 | 0.123 |
| May ‘25 | 6.57 | 0.10 | 1.02 | 0.212 |
| June ‘25 | 4.50 | 0.11 | 0.24 | 0.150 |

Table 2: Grassy Gap WWTP Effluent Flow Monthly Statistics.  Total effluent flow volume is measured in million gallons (MG).  Min, max and average daily values are represented in units of millions of gallons per day (MGD).

| Grassy Gap WWTP | Total flow (MG) | Min (MGD) | Max (MGD) | Average (MGD) |
| --- | --- | --- | --- | --- |
| July ‘24 | 1.27 | 0.021 | 0.113 | 0.041 |
| August ‘24 | 0.84 | 0.008 | 0.044 | 0.027 |
| September ‘24 | 0.93 | 0.012 | 0.092 | 0.031 |
| October ‘24 | 0.81 | 0.005 | 0.157 | 0.026 |
| November ‘24 | 0.66 | 0.009 | 0.067 | 0.022 |
| December ‘24 | 1.46 | 0.011 | 0.321 | 0.047 |
| January ‘25 | 1.64 | 0.028 | 0.131 | 0.053 |
| February ‘25 | 2.37 | 0.019 | 0.322 | 0.079 |
| March ‘25 | 0.81 | 0.015 | 0.049 | 0.026 |
| April ‘25 | 1.14 | 0.016 | 0.087 | 0.038 |
| May ‘25 | 2.64 | 0.025 | 0.347 | 0.085 |
| June ‘25 | 1.23 | 0.026 | 0.07 | 0.041 |